## Sheet1 (2)
Sl.No | Service | As per ISRL recommendation | Base Colour | Band Colour | Updated remarks NG
1 | Seal Oil(OL) | Dark Grey | 7021 | NA | Not in use
2 | Dark Oil emulsifier | Blue(47) (Traffic blue) | 5017 | NA | Insulated
3 | Glycol | (luminous)Canary yellow with 1 Pearl gentian blue | 1026 | 5010 | Stainless Steel
4 | Butadiene < 15% | (pastel) Orange with 1 band Pastel Green bands | 2011 | 6019
5 | Butadiene 5- 95% | Orange with 2 Pastel Green bands | 2011 | 6019
6 | Butadiene >95% | Orange with 3 band Pastel Green bands | 2011 | 6019
7 | Ammonia | (luminous)Canary yellow with 1 (steel)blue band | 1026 | 5011 | Base 1014
8 | Sulphuric acid/Acid | Golden yellow with 3 red bands | 1004 | 3001
9 | Latex | Blue(45) | 5015 | NA | Stainless Steel
10 | Evacuation | Orange (19) | 2011 | NA
11 | Activator | Red Orange (23 | 2001 | NA | Stainless Steel 316L
12 | Styrene (SM) | (Zinc)Yellow (16) | 1018 | NA | Base 1014
13 | Oxidant | Brown (35) | 8008 | NA
14 | Serum | Brown (35) | 8008 | NA | Glass spool with blue colour (RAL 5012)
15 | Short-Stop | Gold (Yellow) (28) | 1004 | NA | Stainless Steel 316L
16 | Coagulation Aid | Pink with one black band | 3015 | 9005 | Stainless Steel
17 | Dark Oil | Green (6) | 6001 | NA | Insulated
18 | Soap Solution | Green (6) | 6001 | NA
19 | Sodium Nitrite | Lavender (93) | 4011 | NA
20 | KOH | Lavender with one black band | 4011 | 9005
21 | Tbc(Tc) | Lavender with one yellow band | 4011 | 1026
22 | Silicone | Dark Grey with one black band | 7021 | 9005 | Stainless Steel
23 | Modifier | Dark Grey (39) | 7021 | NA
24 | Defoamer | Dark Grey with two black band | 7021 | 9005
25 | Relief Header(Rh) | Black | 9005 | NA
26 | Blast Water | Dark Yellow(18) |  |  | Base 5015 RAL 1026 Band to be added as colour is same of storm water - To be reviewed
27 | Waste water | Sky blue with 2 Signal red bands | 5015 | 3001
28 | CWS/CSWR | Sky blue with 1 Brown Beige band | 5015 | 1011
29 | Raw water | Sky blue with 1 Black band | 5015 | 9005 | To be reviewed
30 | Treated water | Sky blue with 1 oxide red band | 5015 | 3009 | Stainless steel
31 | Domestic water | Sky blue with 1 green band | 5015 | 6032 | insulated
32 | Cooling water | Sky blue with 1 light brown band | 5015 | 8001
33 | Plant water | Sky blue with 1 signal red band | 5015 | 3001 | To be reviewed
34 | Tempered water | Sky blue with 2 green bands | 5015 | 6032 | Not in use
35 | Storm water(EW) | Follow IS2379 |  |  | Base 5015+2 (8001 band)
36 | Fire water lines,Foam lines& Extinguishers | Post Office red | 3026
37 | Plant air | Sea green with 1 signal red band | 6032 | 3001
38 | Instrument air | Sea green with 1 black band | 6032 | 9005 | Stainless Steel
39 | Nitrogen | Milky white | 9016
40 | O2 Scavanger | Lavender (93) | 4011 |  | Stainless steel
41 | Natural gas/RLNG | Orange with 3 Oxide red bands | 2003 | 3009
42 | MP Steam | Off white/Aluminium with 1 red band | 9006 | 3001 | insulated
43 | LP Steam | Off white/Aluminium with 1 light green band | 9006 | 6027 | insulated
44 | LP Condensate | Sky blue with 1 white band | 5015 | 9010 | insulated
45 | MP Condensate | Sky blue with 3 oxide red band | 5015 | 3009 | insulated
46 | Vessels & Columns | Aluminium | 9006
47 | Heat Exchanger | Heat resistant Aluminium | 9006
48 | Caustic | Golden yellow | 1004 |  | insulated
49 | Hand railing and monkey ladder cage | Fluorescent yellow | 1026
50 | Staircase,Ladder and Walkways | Black | 9005
51 | Load lifting equipment & monorails etc | Leaf brown | 8000
52 | General Structure | Dark grey | 7031
53 | Monorail stopper | signal red | 3001
54 | AM 2 |  |  |  | Stainless steel
55 | Diesel |  |  |  | Red Oxide
56 | MAO |  |  |  | Insulated
57 | SAO |  |  |  | Insulated
58 | Fatty Acid |  |  |  | Stainless steel
59 | Seal Water |  |  |  | RAL 5015
60 | Atmospheric Vent |  |  |  | RAL 9016
61 | Water Drain/Chemical Drain/Oily Drain |  |  |  | RAL 5015